## FLS ITM Audit
Through Education, We Help Keep People Safe.
FLS Inspection, Testing and Maintenance Audit
System | Check For / Requirements For | Status (Pass/Fail/NA) | Deficiencies Observed | Supporting Maintenance Records (Yes/No) | Documents Required to be Produced
Fire doors | Closed, Latched, Closer, Continuity, Label |  |  |  | Work order, fire log book or other document confirming daily checks. Confirm deficiencies remedied.
Fire Dept Access Route | Unobstructed. Signage in place |  |  |  | Work order, fire log book or other document confirming daily checks. Confirm deficiencies remedied.
Exit Signs | Illuminated (internal or external), Type (words or pictogram), Clearly Visible |  |  |  | Work order, fire log book or other document confirming daily checks. Confirm deficiencies remedied.
Fire Alarm AC Power | AC Power Light On |  |  |  | Work order, fire log book or other document confirming daily checks. Confirm deficiencies remedied.
Fire Pump Room | Temperature (when below 0 Celcius) |  |  |  | Work order, fire log book or other document confirming daily checks. Confirm deficiencies remedied.
Hoods, Ducts, Filters | Combustible build up, filter change frequency, cleanliness (Visual check by tenants) |  |  |  | Work order with date/time. Fire logbook. Confirm deficiencies remedied.
Sprinkler Control valves | Valves controlling fire protection water. Ensure all are open (Applies only to sealed valves; supervised/locked require monthly). |  |  |  | Work order with date/time. Fire logbook. Confirm deficiencies remedied.
Fire Pump | Run at rated speed, General operating condition, Note suction and discharge pressure, Oil and priming water levels, Inspect pressure relief valve |  |  |  | Fire pump test records by service provider or CF staff. Confirm deficiencies remedied.
Emergency Generator | Per CSA 282 |  |  |  | Genset test records by service provider/CF staff. Genset Logbook.
Sprinkler Gauges | Dry system, Pre-action system, Deluge system, Standpipe |  |  |  | Work order with date/time. Fire logbook. Confirm deficiencies remedied.
Dry System Drum Drips | Insulation is intact, Heat tracing functional (winter only), Valves are closed, Visible corrosion or similar |  |  |  | Work order with date/time. Fire logbook. Confirm deficiencies remedied.
Fire Protection Water Tanks | Temperature check |  |  |  | Work order with date/time. Fire logbook. Confirm deficiencies remedied.
Elevators | Tests per B-44, In car alarm, Emergency Communication Test |  |  |  | Elevator test records. Confirm deficiencies remedied.
Doors and Door Hardware in Fire Separations | Hardware is operable, Door opens and closes freely, Door latches, No visible damage, All hardware is intact and functional |  |  |  | Work order or Fire logbook with name/date/time. Confirm deficiencies remedied.
Emergency Lighting Equipment including Exit Signs | Check power on light, Check lamps/bulbs are in place, Damage free, Unplug unit and confirm operation |  |  |  | Work order or Fire logbook with name/date/time. Confirm deficiencies remedied.
Fire Extinguishers | Check monthly tag, Identify if electronic or manual, Check for indicator within green window, Mounted correctly, Damage free, Accessible |  |  |  | Fire extinguisher electronic bar code scans summary or service company records.
Fire Alarm and Voice Communication | Per ULC-S536 (correct edition), emergency power, rotational basis, operation and annunciation, emergency telephone, voice paging, monitoring received alarm |  |  |  | ULC-S536 test record with date/time, initiating zones tested, circuits operated, battery test.
Hose Stations | Hose racked properly, Hose nozzle present/damage free, Valve wrench provided, Gauges in place and functional, Unobstructed and damage free |  |  |  | Work order or Fire logbook with name/date/time. Confirm deficiencies remedied.
Sprinkler control valves | Same as weekly – the 4th weekly inspection covers this item |  |  |  | Work order or Fire logbook with name/date/time. Confirm deficiencies remedied.
Fire Protection Water Tanks | Temperature check |  |  |  | Work order or Fire logbook with name/date/time. Confirm deficiencies remedied.
Emergency Generator | Refer to CSA 282, Operate at 30% load |  |  |  | Genset test records by service provider/CF staff. Genset Logbook.
Sprinkler Alarm Valve - Alarm Test Line | Operate test line on alarm valves and confirm operation of alarm device on alarm line (Applies only if monitored) |  |  |  | Work order or Fire logbook with name/date/time. Confirm deficiencies remedied.
Special Fire Suppression | Refer to appropriate NFPA standard for type of system installed |  |  |  | Special extinguishing system service provider test records.
Water Flow Transmitters Electrical Supervision (ONTARIO ONLY) | Test electrical supervision of each device by operating the device and confirming supervisory condition at monitoring panel. |  |  |  | Work order or Fire logbook confirming tests. Confirm deficiencies remedied.
Fire Drill (buildings over 36m tall) | Fire Drill for supervisory staff (Table top exercise or actual fire drill) |  |  |  | Fire drill report form indicating participants, date/time, alarm initiated, etc.
Fire Department Connection | Check for corrosion, Caps in place and wrench tight, Clear Access |  |  |  | Work order or Fire logbook with name/date/time.
Water flow alarm and supervisory alarm (NFPA 25) | Flow water from inspectors test connection, Operate valves to confirm valve opens and closes. |  |  |  | Service provider test records of waterflow alarm tests. Delay times recorded.
Hydraulic name plates | Check to ensure they are securely attached to risers/alarm valves |  |  |  | Work order or Fire logbook with name/date/time.
Elevators | Test door opening devices, Test key operates switches, Refer to B-44 (NOTE: In Ontario, this requirement is MONTHLY) |  |  |  | Elevator test records by service provider/CF staff.
Smoke Control | Test per Design engineer’s document. Confirm stair, vestibule, elevator shaft pressurization. Confirm smoke exhaust/venting. Confirm recirculating fans shut down. |  |  |  | Smoke control system testing contractor records identifying each test and results.
Fire Separations and Fire Stop Systems | Intact, free of damage? Fire stop material removed? Unprotected penetrations? Closures/doors tight fitting? Smoke seals in place? |  |  |  | Identify all fire separations checked, location, and type. Confirm deficiencies remedied.
Valve supervisory devices (NFPA 25 ONLY) | Test each valve supervisory device for electrical supervision by operating device and confirming on fire alarm panel. |  |  |  | Sprinkler/fire alarm contractor test report of valves operated.
Generator | Refer to CSA 282. Check crankcase breathers, governors, linkages. |  |  |  | Genset test records by service provider/CF staff.
Special Suppression Systems | Consult NFPA standard. Confirm cleaning of exhaust hoods, grease removal device maintenance, overall condition. |  |  |  | Special extinguishing system service provider test records.
Flammable and Combustible Liquids | Confirm quantities/classes in suitable cabinets, SDS sheets available, cabinets ULC listed. |  |  |  | SDS sheets. Flammable/combustible cabinet ULC listing sheet.
Fire dampers and Fire Stop Flaps | Damper type, Damper alignment, Damper integrity (frame, fusible link, overall condition) |  |  |  | Mechanical contractor documentation confirming damper inspections and tests.
Chimney Flues and Flue Pipes | Accumulation of combustibles, Blockages, Overall condition |  |  |  | Chimney contractor documentation confirming inspections and tests.
Disconnect switches for HVAC equipment | Ensure each one is tested by operating the disconnect switch |  |  |  | Electrical contractor documentation confirming each switch tested.
Emergency Lighting Unit Equipment including Exit Signs | Tested for full duration of batteries, Confirm charging circuit is working, Confirm battery/terminal inspection |  |  |  | Emergency lighting contractor test records identifying locations and battery duration tests.
Fire Extinguishers | Tests carried out per NFPA 10, Tags are signed indicating annual maintenance is complete |  |  |  | Fire extinguisher bar code scans summary or service company records.
Fire Alarm and Voice Communication System | Tests per ULC-S536. Confirm monitoring tested per ULC. Check deficiencies fixed. Technician signature/registration. |  |  |  | ULC-S536 test records for annual test, control unit, emergency power, speakers.
Fire Department Connections | Remove caps, check for rust/wear/obstructions. Unobstructed access. Hydrostatic test of dry portion if >30 years old. |  |  |  | Standpipe/Sprinkler contractor test records.
Standpipe Systems | Tests per NFPA 25. Hose is intact, not worn, with nozzle. Hose valves do not leak. Flow test pressure reducing fittings. |  |  |  | Standpipe contractor test records with pressure readings.
Sprinkler Systems | Test per NFPA 25. Flow each system from Inspectors test Connection, Test main drain, Operate valves, Check hangers/bracing/sprinklers. |  |  |  | Sprinkler contractor test records with pressure readings and PIVs identified.
Backflow Preventer | Was test carried out per NFPA 25? Pressure readings recorded? |  |  |  | Sprinkler contractor test records.
Fire Pump | Refer to NFPA 20 and 25. Test at full rated capacity to three design points on certified pump curve. |  |  |  | Fire pump contractor test records identifying curve design points.
Generator | Refer to CSA 282. Test full load for 2 hour duration. Replenish fuel/filters. Check connected light fixtures/exit signs. |  |  |  | Genset test records identifying tests on emergency power and duration.
Special Suppression Systems | Refer to Appropriate NFPA Standard |  |  |  | Special extinguishing system service provider test records.
Fire Drill | Conduct a fire drill. Live drill? Silent drill? Table top exercise? |  |  |  | Fire drill report form indicating participants, date/time, alarm type.
Fire Safety Plan | Review fire safety plan to ensure it is up to date. Confirm FSP approved by local Fire Services. |  |  |  | Copy of approved fire safety plan.
Fire Hydrants | Full flow test conducted, Colour marking match flow, Free of damage, Accessible, Valves fully closed/opened |  |  |  | Fire hydrant test contractor records (method of test, location, make/model).
Post Indicating Valves/Curb Valves | Confirm locking/supervision, Free of damage, Accessible, Fully closed/open test, Confirm left open |  |  |  | Sprinkler contractor test records.
Egress Doors (Electromagnetic Locks, Sliding & Revolving Doors) | Annual testing of electromagnetic locks, sliding doors, and revolving doors per Fire Code updates to ensure proper release/operation. |  |  |  | Contractor or CF staff test records confirming proper operation and release mechanisms.
Dry Sprinkler Systems | Full dry trip of system, Confirm system and low points drained |  |  |  | Sprinkler service contractor test report of dry valves trip tested.
Interior Fire Protection Water Tanks | Refer to NFPA 25 for tanks with corrosion protection |  |  |  | Water tank contractor documents confirming tank interior inspection.
Dry Standpipe System | Refer to NFPA 25. Perform hydrostatic test |  |  |  | Sprinkler service contractor test report of hydrostatic test.
Generator | Refer to CSA 282 |  |  |  | Genset test records by service provider/CF staff.
Dry/Pre-action Sprinkler System | Refer to NFPA 25. Perform obstruction test |  |  |  | Sprinkler service contractor test report of obstruction test.
Wet Sprinkler System | Refer to NFPA 25. Perform obstruction test of 50% of system for large buildings |  |  |  | Sprinkler service contractor test report of obstruction test.
Dry Sprinkler System (Ontario Only) | Inspect for obstructions. Burlap bag test completed. System Flushed |  |  |  | Sprinkler service contractor test report of obstruction test and flushing.
Health and Safety Management College
100 Bronte Road, Unit 11, Oakville ON L6L 6L5 ¦ Phone: 416-282-4764 ¦ Toll Free: 1-877-905-2040
hsmcollege.ca ¦ info@hsmcollege.ca
SAMPLE